## Facilities
FacilityName | PermitID | Permitted_Capacity_MGD | City | State
69th Street Wastewater Treatment Plant | TX0024546 | 80 | Houston | TX
Almeda Sims Wastewater Treatment Plant | TX0024589 | 34 | Houston | TX
Buffalo Bayou Treatment Plant | TX0024449 | 100 | Houston | TX
Settegast Wastewater Treatment Plant | TX0024341 | 70 | Houston | TX

## Composition
Parameter | Unit | Raw_Influent | Secondary_Effluent | Post_UF_Treatment | Post_RO_Treatment | DC_Cooling_Water_Required | Source
Flow Rate (Average) | MGD (Million Gallons/Day) | 160 | 160 | 148 | 111 | N/A | Houston City Annual Water Report
Flow Rate (Peak) | MGD | 200 | 200 | 185 | 139 | N/A | Houston WWTP Design Data
BOD (5-day) | mg/L | 250 | <20 | <5 | <1 | N/A | EPA Secondary Treatment Standards
TSS (Total Suspended Solids) | mg/L | 220 | <20 | <2 | <0.5 | <5 | EPA Secondary Treatment Standards
TDS (Total Dissolved Solids) | mg/L | 750 | 700–900 | 700–900 | 50–150 | <200 | TCEQ Permits & EPA ECHO
Conductivity | µS/cm | 1200 | 1100–1300 | 1100–1300 | 100–250 | <500 | TCEQ Permits & EPA ECHO
Ammonia (as N) | mg/L | 35 | 8–12 | <1 | <0.1 | N/A | EPA ECHO DMR - Parameter 00610
Nitrate (as N) | mg/L | 2 | 2–4 | 2–4 | <0.1 | N/A | EPA ECHO DMR - Parameter 00620
Total Phosphorus | mg/L | 8 | 4–7 | 4–7 | <0.5 | N/A | EPA ECHO DMR - Parameter 00665
Hardness (as CaCO3) | mg/L | 200 | 200–250 | 200–250 | <20 | <100 | USGS Harris County Water Quality
Chloride | mg/L | 150 | 150–180 | 150–180 | <20 | <100 | USGS Harris County Water Quality
Sulfate | mg/L | 100 | 100–120 | 100–120 | <10 | N/A | USGS Harris County Water Quality
Silica (SiO2) | mg/L | 20 | 20–25 | 20–25 | <5 | <30 | USGS Harris County Water Quality
pH | pH units | 7.2–7.8 | 7.0–8.0 | 7.0–8.0 | 6.5–7.5 | 6.5–8.5 | EPA Standards
Temperature | °C | 18–25 | 18–25 | 18–25 | 18–25 | N/A | Typical Municipal WW
Turbidity | NTU | 100–200 | <5 | <0.5 | <1 | <1 | EPA Standards

## Treatment_Costs
Treatment_Type | Capital_Cost_Per_MGD | Operating_Cost_Per_1000_Gal | Recovery_Rate | Efluent_TDS | Data_Source
Ultrafiltration (UF) Only | 1500000 | 0.75 | 0.925 | 500–800 ppm | EPA Water Reuse Guidelines 2022
Reverse Osmosis (RO) Only | 2000000 | 1.25 | 0.75 | <100 ppm | EPA Water Reuse Guidelines 2022
UF + RO (Combined) | 3200000 | 1.85 | 0.69 | <50 ppm | EPA Water Reuse Guidelines 2022
Advanced Oxidation Process (AOP) | 1800000 | 0.95 | 0.9 | <100 ppm | TWDB Case Studies
UV + GAC | 1200000 | 0.6 | 0.95 | <200 ppm | EPA Standards
Conventional Activated Sludge | 1000000 | 0.4 | 0.95 | <500 ppm | EPA Standards
Membrane Bioreactor (MBR) | 2500000 | 0.85 | 0.92 | <300 ppm | EPA Water Reuse Guidelines 2022

## Water_Rates
Rate_Type | Rate_2024 | Annual_Cost_For_1MGD | Source
Residential (per 1,000 gal) | 11.97 | 11970000 | Houston Public Works Rate Schedule 2024
Commercial/Industrial (per 1,000 gal) | 12.45 | 12450000 | Houston Public Works Rate Schedule 2024
Irrigation (per 1,000 gal) | 11.2 | 11200000 | Houston Public Works Rate Schedule 2024
Bulk Reclaimed Water (per 1,000 gal) | 5.5 | 5500000 | Texas Water Development Board
Sewer (per 1,000 gal) | 8.75 | 8750000 | Houston Public Works Rate Schedule 2024
Stormwater (monthly base) | 15 |  | Houston Public Works Rate Schedule 2024

## DC_Cooling_Requirements
Parameter | Min_Value | Max_Value | Standard | RO_Treated_Water_Meets
TDS (Total Dissolved Solids) | <50 | <200 | ASHRAE 1079 | ✅ <50 ppm TDS
Conductivity | 200–500 | <3000 | ASHRAE 1079 | ✅ <250 µS/cm
pH | 6.5 | 8.5 | ASHRAE 1079 | ✅ 6.5–7.5
Hardness (as CaCO3) | 30 | <200 | ASHRAE 1079 | ✅ <20 ppm
Silica (SiO2) | <15 | <50 | ASHRAE 1079 | ✅ <1 ppm
Iron (Fe) | <0.3 | <1.0 | ASHRAE 1079 | ✅ <0.1 ppm
Chloride | <100 | <150 | ASHRAE 1079 | ✅ <10 ppm
Sulfate | <50 | <100 | ASHRAE 1079 | ✅ <5 ppm
Ammonia (N) | <0.5 | <2 | ASHRAE 1079 | ✅ <0.1 ppm
Copper | <0.1 | <0.5 | ASHRAE 1079 | ✅ <0.01 ppm
Turbidity | <1 | <5 | ASHRAE 1079 | ✅ <1 NTU
Cooling Tower Cycles of Concentration | 6–10 | Variable | ASHRAE Handbook | ✅ 10+ cycles possible

## Economic_Analysis
Metric | Value
Annual Demand | 15 MGD
Potable Water Rate | $11.97/1000 gal
UF/RO Treated Water Cost | $1.85/1000 gal
Annual Potable Cost | $65,535,750
Annual Reclaimed Water Cost | $10,128,750
Annual Savings | $55,407,000
Payback Period (Capital) | 316.2 years
ROI (10 years) | 1154.3%